## Revision Changes
From | To | Changes
A | 0 | Issued for Information
0 | 1 | Revised with Orignal Stream data | JJM | 2019-04-30
1 | 2 | Released as project documentation | JJM
2 | 3 | As Programmed | DD | 2020-06-19

## PPF_CLIENT_Datamap
| ENCANA - PIPESTONE PPF MODBUS MAP | [12 empty] | REV 3
| Tag Number | PLC Tag | Service Description (Max=32 Characters) | Data Type | Read/Write | PLC ModBus Address | Bit | Min Range | Max Range | Eng Unit | STATUS 0 | STATUS 1 | Comments | P&ID COMMENT | Verfied By
1 | RESET | RESET | Reset Alarm | BOOL | WRITE | 00001 | N/A | N/A | N/A | N/A | OFF | RESET | Pulse for 2 seconds to reset latched alarms
2 | OBC_COMM_FAIL | OBC_COMM_FAIL | On Board Computer Communication Fault | BOOL | READ | 00002 | N/A | N/A | N/A | N/A | FAULT | OK | Indicates failure between On Board Computer and PLC
3 | STREAM - 1
4 | UA_3108A | Stream_1_Analyzer_Warning | Stream 1-Analyzer Common Warning Alarm | BOOL | READ | 00010 | N/A | N/A | N/A | N/A | OFF | WARNING | Warning Local To Analyzer Control Cabinet
5 |  | Stream_1_Model_Warning | Stream 1 - Analyzer Model Quality Warning | BOOL | READ | 00011 | N/A | N/A | N/A | N/A | OFF | WARNING | Calibration Quality
6 | UA_3108B | Stream_1_Sample_Panel_Warning | Stream 1-Sample Panel Common Warning Alarm | BOOL | READ | 00012 | N/A | N/A | N/A | N/A | OFF | WARNING | Warning Local To Sample System Enclosure
7 | FSL_3108 | Stream_1_FSL_COND | Stream 1 - Low Sample Flow Warning | REAL | READ | 00013 | N/A | N/A | N/A | N/A | OFF | WARNING | No Flow Condition at Sample Cell
8 | FSH_3108 | Stream_1_FSH_COND | Stream 1 - High Sample Flow Warning | REAL | READ | 00014 | N/A | N/A | N/A | N/A | OFF | WARNING | Hi Flow Condition at Sample Cell
9 | PAH-3108 | Stream_1_High_Pressure_Alarm | Stream 1 - High Pressure Warning Alarm | BOOL | READ | 00015 | N/A | N/A | N/A | N/A | OFF | WARNING | Setpoint Local to HMI
10 | TAH-3108 | Stream_1_High_Temperature_Alarm | Stream 1 - High Temperature Warning Alarm | BOOL | READ | 00016 | N/A | N/A | N/A | N/A | OFF | WARNING | Setpoint Local to HMI
11 |  | Stream_1_Sampling_Alarm | Stream 1 - Sample Switch Warning | BOOL | READ | 00017 | N/A | N/A | N/A | N/A | OFF | WARNING | Left in SAMPLE mode > 20 min
12 | XA_3108A | Stream_1_Analyzer_Fault | Stream 1-Analyzer Common Fault Alarm | BOOL | READ | 00018 | N/A | N/A | N/A | N/A | OFF | FAULT | Faut Local To Analyzer Control Cabinet
13 |  | Stream_1_Model_Fault | Stream 1 - Analyzer Model Quality Fault | BOOL | READ | 00019 | N/A | N/A | N/A | N/A | OFF | FAULT | Calibration Quality
14 | XA_3108B | Stream_1_Sample_Panel_Fault | Stream 1-Sample Panel Common Fault Alarm | BOOL | READ | 00020 | N/A | N/A | N/A | N/A | OFF | FAULT | Faut Local To Sample System Enclosure
15 |  | Stream_1_Flow_Fault | Stream 1 - Flow Transmitter Fault | BOOL | READ | 00021 | N/A | N/A | N/A | N/A | OFF | FAULT | Hardware Fault | Not Used
16 |  | Stream_1_Temperature_Fault | Stream 1 - Temperature Transmitter Fault | BOOL | READ | 00022 | N/A | N/A | N/A | N/A | OFF | FAULT | Hardware Fault
17 |  | Stream_1_Pressure_Fault | Stream 1 - Pressure Transmitter Fault | BOOL | READ | 00023 | N/A | N/A | N/A | N/A | OFF | FAULT | Hardware Fault
18 | STREAM - 2
19 | UA_4107A | Stream_2_Analyzer_Warning | Stream 2-Analyzer Common Warning Alarm | BOOL | READ | 00050 | N/A | N/A | N/A | N/A | OFF | WARNING | Warning Local To Analyzer Control Cabinet
20 |  | Stream_2_Model_Warning | Stream 2 - Analyzer Model Quality Warning | BOOL | READ | 00051 | N/A | N/A | N/A | N/A | OFF | WARNING | Calibration Quality
21 | UA-4107B | Stream_2_Sample_Panel_Warning | Stream 2-Sample Panel Common Warning Alarm | BOOL | READ | 00052 | N/A | N/A | N/A | N/A | OFF | WARNING | Warning Local To Sample System Enclosure
22 | FSL_4107 | Stream_2_FSL_COND | Stream 2 - Low Sample Flow Warning | REAL | READ | 00053 | N/A | N/A | N/A | N/A | OFF | WARNING | No Flow Condition at Sample Cell
23 | FSH-4107 | Stream_2_FSH_COND | Stream 2 - High Sample Flow Warning | REAL | READ | 00054 | N/A | N/A | N/A | N/A | OFF | WARNING | Hi Flow Condition at Sample Cell
24 | PAH-4107 | Stream_2_High_Pressure_Alarm | Stream 2 - High Pressure Warning Alarm | BOOL | READ | 00055 | N/A | N/A | N/A | N/A | OFF | WARNING | Setpoint Local to HMI
25 | TAH-4107 | Stream_2_High_Temperature_Alarm | Stream 2 - High Temperature Warning Alarm | BOOL | READ | 00056 | N/A | N/A | N/A | N/A | OFF | WARNING | Setpoint Local to HMI
26 |  | Stream_2_Sampling_Alarm | Stream 2 - Sample Switch Warning | BOOL | READ | 00057 | N/A | N/A | N/A | N/A | OFF | WARNING | Left in SAMPLE mode > 20 min
27 | XA-4107A | Stream_2_Analyzer_Fault | Stream 2-Analyzer Common Fault Alarm | BOOL | READ | 00058 | N/A | N/A | N/A | N/A | OFF | FAULT | Faut Local To Analyzer Control Cabinet
28 |  | Stream_2_Model_Fault | Stream 2 - Analyzer Model Quality Fault | BOOL | READ | 00059 | N/A | N/A | N/A | N/A | OFF | FAULT | Calibration Quality
29 | XA-4107B | Stream_2_Sample_Panel_Fault | Stream 2-Sample Panel Common Fault Alarm | BOOL | READ | 00060 | N/A | N/A | N/A | N/A | OFF | FAULT | Faut Local To Sample System Enclosure
30 |  | Stream_2_Flow_Fault | Stream 2 - Flow Transmitter Fault | BOOL | READ | 00061 | N/A | N/A | N/A | N/A | OFF | FAULT | Hardware Fault | Not Used
31 |  | Stream_2_Temperature_Fault | Stream 2 - Temperature Transmitter Fault | BOOL | READ | 00062 | N/A | N/A | N/A | N/A | OFF | FAULT | Hardware Fault
32 |  | Stream_2_Pressure_Fault | Stream 2 - Pressure Transmitter Fault | BOOL | READ | 00063 | N/A | N/A | N/A | N/A | OFF | FAULT | Hardware Fault
33 | Holding Registers
34 | CT_3112 | CT_3112 | Communications Heartbeat Register to DCS | INT | READ | 40001 | N/A | 0 | 60 | N/A | N/A | N/A | PLC Clock Seconds passed onto master controller. Alarm if value has not changed after set time. | A communications failure will interupt both channels.
35 | STREAM - 1
36 | PIT-3108 | Stream_1_Pressure_1 | Stream 1, Pressure | REAL | READ | 40010 | N/A | 0 | 3500 | kPag | N/A | N/A
37 | TIT-3108 | Stream_1_Temperature_1 | Stream 1, Temperature | REAL | READ | 40012 | N/A | -20 | 80 | C | N/A | N/A
38 | AIT-3108A | Stream_1_Deemed C4 | Stream 1, Deemed C4- calculated as: Deemed C4- = (3*(%C1+%C2+%C3)) + (%iC4+%nC4) | REAL | READ | 40014 | N/A | 0 | 100 | % | N/A | N/A
39 | AIT-3108B | Stream_1_C1 (Vol%) | Stream 1, C1 | REAL | READ | 40016 | N/A | 0 | 100 | VOL% | N/A | N/A
40 | AIT-3108C | Stream_1_C2 (Vol%) | Stream 1, C2 | REAL | READ | 40018 | N/A | 0 | 100 | VOL% | N/A | N/A
41 | AIT-3108D | Stream_1_C3 (Vol%) | Stream 1, C3 | REAL | READ | 40020 | N/A | 0 | 100 | VOL% | N/A | N/A
42 | AIT-3108E | Stream_1_iC4 (Vol%) | Stream 1, iC4 | REAL | READ | 40022 | N/A | 0 | 100 | VOL% | N/A | N/A
43 | AIT-3108F | Stream_1_nC4 (Vol%) | Stream 1, nC4 | REAL | READ | 40024 | N/A | 0 | 100 | VOL% | N/A | N/A
44 | AIT-3108G | Stream_1_C5+ (Vol%) | Stream 1, C5 Plus | REAL | READ | 40026 | N/A | 0 | 100 | VOL% | N/A | N/A
45 |  |  | Spare | REAL | READ | 40028 | N/A | 0 | 100 | VOL% | N/A | N/A
46 |  |  | Spare | REAL | READ | 40030 | N/A | 0 | 100 | VOL% | N/A | N/A
47 | AIT-3108J | Stream_1_C1 (Mol%) | Stream 1, C1 | REAL | READ | 40032 | N/A | 0 | 100 | MOL% | N/A | N/A
48 | AIT-3108K | Stream_1_C2 (Mol%) | Stream 1, C2 | REAL | READ | 40034 | N/A | 0 | 100 | MOL% | N/A | N/A
49 | AIT-3108L | Stream_1_C3 (Mol%) | Stream 1, C3 | REAL | READ | 40036 | N/A | 0 | 100 | MOL% | N/A | N/A
50 | AIT-3108M | Stream_1_iC4 (Mol%) | Stream 1, iC4 | REAL | READ | 40038 | N/A | 0 | 100 | MOL% | N/A | N/A
51 | AIT-3108N | Stream_1_nC4 (Mol%) | Stream 1, nC4 | REAL | READ | 40040 | N/A | 0 | 100 | MOL% | N/A | N/A
52 | AIT-3108O | Stream_1_iC5 (Mol%) | Stream 1, iC5 | REAL | READ | 40042 | N/A | 0 | 100 | MOL% | N/A | N/A
53 | AIT-3108P | Stream_1_nC5 (Mol%) | Stream 1, nC5 | REAL | READ | 40044 | N/A | 0 | 100 | MOL% | N/A | N/A
54 | AIT-3108Q | Stream_1_C6 (Mol%) | Stream 1, C6 | REAL | READ | 40046 | N/A | 0 | 100 | MOL% | N/A | N/A
55 | AIT-3108R | Stream_1_C7 (Mol%) | Stream 1, C7 | REAL | READ | 40048 | N/A | 0 | 100 | MOL% | N/A | N/A
56 | AIT-3108S | Stream_1_C8 (Mol%) | Stream 1, C8 | REAL | READ | 40050 | N/A | 0 | 100 | MOL% | N/A | N/A
57 | AIT-3108T | Stream_1_C9 (Mol%) | Stream 1, C9 | REAL | READ | 40052 | N/A | 0 | 100 | MOL% | N/A | N/A
58 | AIT-3108U | Stream_1_C10 (Mol%) | Stream 1, C10 | REAL | READ | 40054 | N/A | 0 | 100 | MOL% | N/A | N/A
59 | AIT-3108V | Stream_1_C11 (Mol%) | Stream 1, C11 | REAL | READ | 40056 | N/A | 0 | 100 | MOL% | N/A | N/A
60 | AIT-3108W | Stream_1_C12 (Mol%) | Stream 1, C12 | REAL | READ | 40058 | N/A | 0 | 100 | kPag | N/A | N/A
61 |  |  | Spare | REAL | READ | 40060 | N/A | 0 | 150 | kPag | N/A | N/A
62 | AIT-3108Y | Stream_1_Stream_1_Transmission | Stream 1, Transmission | REAL | READ | 40062 | N/A | 0 | 100 | % | N/A | N/A | Analyzer Diagnostic Signal
63 | Stream - 2
64 | PIT-4104 | Stream_2_Pressure | Stream 2, Pressure | REAL | READ | 40110 | N/A | 0 | 3500 | kPag | N/A | N/A
65 | TIT-4107 | Stream_2_Temperature | Stream 2, Temperature | REAL | READ | 40112 | N/A | -20 | 80 | C | N/A | N/A
66 | AIT-4107A | Stream_2_C2_C3_Ratio | Stream 2, C2/C3 Ratio | REAL | READ | 40114 | N/A | 0 | 100 | % | N/A | N/A
67 | AIT-4107B | Stream_2_C1 (Mol%) | Stream 2, C1 | REAL | READ | 40116 | N/A | 0 | 100 | VOL% | N/A | N/A
68 | AIT-4107C | Stream_2_C2 (Mol%) | Stream 2, C2 | REAL | READ | 40118 | N/A | 0 | 100 | VOL% | N/A | N/A
69 | AIT-4107D | Stream_2_C3 (Mol%) | Stream 2, C3 | REAL | READ | 40120 | N/A | 0 | 100 | VOL% | N/A | N/A
70 | AIT-4107E | Stream_2_iC4 (Mol%) | Stream 2, iC4 | REAL | READ | 40122 | N/A | 0 | 100 | VOL% | N/A | N/A
71 | AIT-4107F | Stream_2_nC4 (Mol%) | Stream 2, nC4 | REAL | READ | 40124 | N/A | 0 | 100 | VOL% | N/A | N/A
72 | AIT-4107G | Stream_2_iC5 (Mol%) | Stream 2, iC5 | REAL | READ | 40126 | N/A | 0 | 100 | VOL% | N/A | N/A
73 | AIT-4107H | Stream_2_nC5 (Mol%) | Stream 2, nC5 | REAL | READ | 40128 | N/A | 0 | 100 | VOL% | N/A | N/A
74 | AIT-4107I | Stream_2_C6+ (Mol%) | Stream 2, C6 plus | REAL | READ | 40130 | N/A | 0 | 100 | VOL% | N/A | N/A
75 | AIT-4107Q | Stream_2_C1_C3_Ratio | Stream 2, C1/C3 Ratio | REAL | READ | 40132 | N/A | 0 | 100 | MOL% | N/A | N/A
76 | AIT-4107Q | Stream_2_Transmission | Stream 2, Transmission | REAL | READ | 40136 | N/A | 0 | 100 | MOL% | N/A | N/A
Blue fill denotes tags that customer will pull back to their control system.

## DataTypes (hidden)
Data Type | Description
BOOL | Boolean, Single bit
WORD | Unsigned 16 bit value bit 0 is the low bit bit 15 is the high bit
SHORT | Signed 16 bit value bit 0 is the low bit bit 14 is the high bit bit 15 is the sign bit
DWORD | Unsigned 32 bit value bit 0 is the low bit bit 31 is the high bit
LONG | Signed 32 bit value bit 0 is the low bit bit 30 is the high bit bit 31 is the sign bit
BCD | Two byte packed BCD Value range is 0-9999. Behavior is undefined for values beyond this range.
LBCD | Four byte packed BCD Value range is 0-99999999. Behavior is undefined for values beyond this range.
STRING | Null terminated ASCII string Supported on Modbus Model, includes Hi-Lo Lo-Hi byte order selection.
DOUBLE (Note 1) | 64 bit floating point value The driver interprets four consecutive registers as a double precision value by making the last two registers the high DWord and the first two registers the low DWord.
DOUBLE Example | If register 40001 is specified as a double, bit 0 of register 40001 would be bit 0 of the 64 bit data type and bit 15 of register 40004 would be bit 63 of the 64 bit data type.
FLOAT (Note 1) | 32 bit floating point value The driver interprets two consecutive registers as a single precision value by making the last register the high word and the first register the low word.
FLOAT Example | If register 40001 is specified as a float, bit 0 of register 40001 would be bit 0 of the 32 bit data type and bit 15 of register 40002 would be bit 31 of the 32 bit data type.
Notes:
1. The descriptions assume the default; that is, first DWord low data handling of 64 bit data types and first word
low data handling of 32 bit data types.
2. Standard data format names have been selected. If other names are desired, specify the bytes and range.