## PLC MODBUS MAP
OVINTIV - PIPESTONE PPF MODBUS MAP | [12 empty] | UPGRADE 2025-01-28
Tag Number | PLC Tag | Service Description (Max=32 Characters) | Data Type | Read/Write | OBC ModBus Address | PLC ModBus Address | Bit | Min Range | Max Range | Eng Unit | STATUS 0 | STATUS 1 | Comments | ADDITIONAL COMMENTS
RESET | RESET | Reset Alarm | BOOL | WRITE |  | 00001 | N/A | N/A | N/A | N/A | OFF | RESET | Not used on this system | All latching alarms have been removed
OBC_COMM_FAIL | OBC_COMM_FAIL | On Board Computer Communication Fault | BOOL | READ |  | 00002 | N/A | N/A | N/A | N/A | WARNING | NORMAL | Indictes that the analyzer has not performed an analysis in the last 20 minutes
| PLC_Forced | PLC Forced | BOOL | READ |  | 00003 | N/A | N/A | N/A | N/A | WARNING | OK
| spareCoil | Spare Coil | BOOL | READ |  | 00004 | N/A | N/A | N/A | N/A | N/A | N/A
| spareCoil | Spare Coil | BOOL | READ |  | 00005 | N/A | N/A | N/A | N/A | N/A | N/A
| spareCoil | Spare Coil | BOOL | READ |  | 00006 | N/A | N/A | N/A | N/A | N/A | N/A
| spareCoil | Spare Coil | BOOL | READ |  | 00007 | N/A | N/A | N/A | N/A | N/A | N/A
| spareCoil | Spare Coil | BOOL | READ |  | 00008 | N/A | N/A | N/A | N/A | N/A | N/A
| spareCoil | Spare Coil | BOOL | READ |  | 00009 | N/A | N/A | N/A | N/A | N/A | N/A
STREAM - 1
UA_3108A | Stream_1_Analyzer_Warning | Stream 1-Analyzer Common Warning Alarm | BOOL | READ |  | 00010 | N/A | N/A | N/A | N/A | OFF | WARNING | Common warning generated by analyzer software | Contact Insight/JP3 to diagnose warning
| Stream_1_Model_Warning | Stream 1 - Model Quality Warning | BOOL | READ |  | 00011 | N/A | N/A | N/A | N/A | OFF | WARNING | Calibration Warning | Analyzer is operating at the edge of calibrated range. Add more samples to extend range.
| spareBool | Spare Coil | BOOL | READ |  | 00012 | N/A | N/A | N/A | N/A | OFF | WARNING
FSL_3108 | Stream_1_FSL_COND | Stream 1 - Low Sample Flow Warning | REAL | READ |  | 00013 | N/A | N/A | N/A | N/A | OFF | WARNING | 5 sec debounce
FSH_3108 | Stream_1_FSH_COND | Stream 1 - High Sample Flow Warning | REAL | READ |  | 00014 | N/A | N/A | N/A | N/A | OFF | WARNING | Removed from logic | Not used on this panel
PAH-3108 | Stream_1_High_Pressure_Alarm | Stream 1 - High Pressure Warning Alarm | BOOL | READ |  | 00015 | N/A | N/A | N/A | N/A | OFF | WARNING | 5 sec debounce
TAH-3108 | Stream_1_High_Temperature_Alarm | Stream 1 - High Temperature Warning Alarm | BOOL | READ |  | 00016 | N/A | N/A | N/A | N/A | OFF | WARNING | 30 sec debounce | No flow to sample panel. Check sample loop,
| Stream_1_Sampling_Alarm | Stream 1 - Sample Switch Warning | BOOL | READ |  | 00017 | N/A | N/A | N/A | N/A | OFF | WARNING | Removed from logic | Not used on this panel
XA_3108A | Stream_1_Analyzer_Fault | Stream 1-Analyzer Common Fault Alarm | BOOL | READ |  | 00018 | N/A | N/A | N/A | N/A | OFF | FAULT | Common fault generated by analyzer software | Contact Insight/JP3 to diagnose fault
| Stream_1_Model_Fault | Stream 1 - Model Quality Fault | BOOL | READ |  | 00019 | N/A | N/A | N/A | N/A | OFF | FAULT | Calibration Fault | Analyzer software can not calculate a result for one or more components. Contact Insight or JP3
| spareBool | Spare Coil | BOOL | READ |  | 00020 | N/A | N/A | N/A | N/A | OFF | FAULT
| Stream_1_Spare | Stream 1 - Spare | BOOL | READ |  | 00021 | N/A | N/A | N/A | N/A | OFF | FAULT
| Stream_1_Temperature_Fault | Stream 1 - Temperature Transmitter Fault | BOOL | READ |  | 00022 | N/A | N/A | N/A | N/A | OFF | FAULT | Loss of 4-20 mA signal detected | Check field device for power
| Stream_1_Pressure_Fault | Stream 1 - Pressure Transmitter Fault | BOOL | READ |  | 00023 | N/A | N/A | N/A | N/A | OFF | FAULT | Loss of 4-20 mA signal detected | Check field device for power
| Stream_1_VCON_Normal | Stream 1 - Analyzer In Continous Analysis Mode | BOOL | READ |  | 00024 | N/A | N/A | N/A | N/A | FALSE | TRUE | Sample Collection Control | Status bit for HMI graphics
| Stream_1_VCON_Get_Ready | Stream 1 - Analyzer Sample Collection Mode Request | BOOL | READ |  | 00025 | N/A | N/A | N/A | N/A | FALSE | TRUE | Sample Collection Control | Status bit for HMI graphics
| Stream_1_VCON_Sampling | Stream 1 - Analyzer in Sample Collection Mode | BOOL | READ |  | 00026 | N/A | N/A | N/A | N/A | FALSE | TRUE | Sample Collection Control | Status bit for HMI graphics
| Stream_1_VCON_Ready | Stream 1 - Analyzer Ready For Sample Collection | BOOL | READ |  | 00027 | N/A | N/A | N/A | N/A | FALSE | TRUE | Sample Collection Control | Status bit for HMI graphics
| Stream_1_Sample_Source | Stream 1 - Sample Request Source | BOOL | READ |  | 00028 | N/A | N/A | N/A | N/A | HMI | SWITCH | Sample Control HMI or Handswitch | HMI use only
| Stream_1_Active_Alarm | Stream 1 - Active Alarm | BOOL | READ |  | 00029 | N/A | N/A | N/A | N/A | OFF | ALARM
| Stream_1_Interruption_Valve | Stream 1 - Interrupt Valve | BOOL | READ |  | 00030 | N/A | N/A | N/A | N/A | OFF | ALARM
STREAM - 2
UA_4107A | Stream_2_Analyzer_Warning | Stream 2-Analyzer Common Warning Alarm | BOOL | READ |  | 00050 | N/A | N/A | N/A | N/A | OFF | WARNING | Common warning generated by analyzer software | Contact Insight/JP3 to diagnose warning
| Stream_2_Model_Warning | Stream 2 - Analyzer Model Quality Warning | BOOL | READ |  | 00051 | N/A | N/A | N/A | N/A | OFF | WARNING | Calibration Warning | Analyzer is operating at the edge of calibrated range. Add more samples to extend range.
| spareBool | Spare Coil | BOOL | READ |  | 00052 | N/A | N/A | N/A | N/A | OFF | WARNING
FSL_4107 | Stream_2_FSL_COND | Stream 2 - Low Sample Flow Warning | REAL | READ |  | 00053 | N/A | N/A | N/A | N/A | OFF | WARNING | 5 sec debounce
FSH-4107 | Stream_2_FSH_COND | Stream 2 - High Sample Flow Warning | REAL | READ |  | 00054 | N/A | N/A | N/A | N/A | OFF | WARNING | Removed from logic | Not used on this panel
PAH-4107 | Stream_2_High_Pressure_Alarm | Stream 2 - High Pressure Warning Alarm | BOOL | READ |  | 00055 | N/A | N/A | N/A | N/A | OFF | WARNING | 5 sec debounce
TAH-4107 | Stream_2_High_Temperature_Alarm | Stream 2 - High Temperature Warning Alarm | BOOL | READ |  | 00056 | N/A | N/A | N/A | N/A | OFF | WARNING | 30 sec debounce | No flow to sample panel. Check sample loop,
| Stream_2_Sampling_Alarm | Stream 2 - Sample Switch Warning | BOOL | READ |  | 00057 | N/A | N/A | N/A | N/A | OFF | WARNING | Left in SAMPLE mode > 20 min
XA-4107A | Stream_2_Analyzer_Fault | Stream 2-Analyzer Common Fault Alarm | BOOL | READ |  | 00058 | N/A | N/A | N/A | N/A | OFF | FAULT | Common fault generated by analyzer software | Contact Insight/JP3 to diagnose fault
| Stream_2_Model_Fault | Stream 2 - Analyzer Model Quality Fault | BOOL | READ |  | 00059 | N/A | N/A | N/A | N/A | OFF | FAULT | Calibration Fault | Analyzer software can not calculate a result for one or more components. Contact Insight or JP3
XA-4107B | spareBool | SpareCoil | BOOL | READ |  | 00060 | N/A | N/A | N/A | N/A | OFF | FAULT
| Stream_2_Spare | Stream 2 - Spare | BOOL | READ |  | 00061 | N/A | N/A | N/A | N/A | OFF | FAULT | Hardware Fault | Not Used
| Stream_2_Temperature_Fault | Stream 2 - Temperature Transmitter Fault | BOOL | READ |  | 00062 | N/A | N/A | N/A | N/A | OFF | FAULT | Loss of 4-20 mA signal detected | Check field device for power
| Stream_2_Pressure_Fault | Stream 2 - Pressure Transmitter Fault | BOOL | READ |  | 00063 | N/A | N/A | N/A | N/A | OFF | FAULT | Loss of 4-20 mA signal detected | Check field device for power
| Stream_2_VCON_Normal | Stream 2 - Analyzer In Continous Analysis Mode | BOOL | READ |  | 00064 | N/A | N/A | N/A | N/A | FALSE | TRUE | Sample Collection Control | Status bit for HMI graphics
| Stream_2_VCON_Get_Ready | Stream 2 - Analyzer Sample Collection Mode Request | BOOL | READ |  | 00065 | N/A | N/A | N/A | N/A | FALSE | TRUE | Sample Collection Control | Status bit for HMI graphics
| Stream_2_VCON_Sampling | Stream 2 - Analyzer in Sample Collection Mode | BOOL | READ |  | 00066 | N/A | N/A | N/A | N/A | FALSE | TRUE | Sample Collection Control | Status bit for HMI graphics
| Stream_2_VCON_Ready | Stream 2 - Analyzer Ready For Sample Collection | BOOL | READ |  | 00067 | N/A | N/A | N/A | N/A | FALSE | TRUE | Sample Collection Control | Status bit for HMI graphics
| Stream_2_Sample_Source | Stream 2 - Sample Request Source | BOOL | READ |  | 00068 | N/A | N/A | N/A | N/A | HMI | SWITCH | Sample Control HMI or Handswitch
| Stream_2_Active_Alarm | Stream 2 - Active Alarm | BOOL | READ |  | 00069 | N/A | N/A | N/A | N/A | OFF | ALARM
Holding Registers
CT_3112 | CT_3112 | Communications Heartbeat Register to DCS | INT | READ |  | 40001 | N/A | 0 | 60 | N/A | N/A | N/A | PLC Clock Seconds passed onto master controller. Alarm if value has not changed after set time. | A communications failure will interupt both channels.
PLC_YEAR | PLC_YEAR | PLC Clock Year | INT | READ |  | 40002 | N/A | 0 | 60 | N/A | N/A | N/A | Real Time Clock From PLC
PLC_MONTH | PLC_MONTH | PLC Clock Month | INT | READ |  | 40003 | N/A | 0 | 60 | N/A | N/A | N/A | Real Time Clock From PLC
PLC_DAY | PLC_DAY | PLC Clock Day | INT | READ |  | 40004 | N/A | 0 | 60 | N/A | N/A | N/A | Real Time Clock From PLC
PLC_HOUR | PLC_HOUR | PLC Clock Hour | INT | READ |  | 40005 | N/A | 0 | 60 | N/A | N/A | N/A | Real Time Clock From PLC
PLC_MINUTE | PLC_MINUTE | PLC Clock Minute | INT | READ |  | 40006 | N/A | 0 | 60 | N/A | N/A | N/A | Real Time Clock From PLC
PLC_SECOND | PLC_SECOND | PLC Clock Second | INT | READ |  | 40007 | N/A | 0 | 60 | N/A | N/A | N/A | Real Time Clock From PLC
| STREAMS_ENABLED | Number of Streams on HMI | INT | READ |  | 40008 | N/A | 0 | 60 | N/A | N/A | N/A | Real Time Clock From PLC
| spareInt | Spare Holding Register | INT | READ |  | 40009 | N/A | 0 | 60 | N/A | N/A | N/A | Real Time Clock From PLC
STREAM - 1
PIT-3108 | Stream_1_Pressure_1 | Stream 1, Pressure | REAL | READ | 7049 | 40010 | N/A | 0 | 3500 | kPag | N/A | N/A
TIT-3108 | Stream_1_Temperature_1 | Stream 1, Temperature | REAL | READ | 7051 | 40012 | N/A | -20 | 80 | C | N/A | N/A
AIT-3108A | Stream_1_Deemed C4 | Stream 1, Deemed C4- | REAL | READ | 7017 | 40014 | N/A | 0 | 100 | % | N/A | N/A | Calculated as (C1 +C2+C3)*3+iC4+nC4
AIT-3108B | Stream_1_C1 (Vol%) | Stream 1, C1 | REAL | READ | 7001 | 40016 | N/A | 0 | 100 | VOL% | N/A | N/A
AIT-3108C | Stream_1_C2 (Vol%) | Stream 1, C2 | REAL | READ | 7003 | 40018 | N/A | 0 | 100 | VOL% | N/A | N/A
AIT-3108D | Stream_1_C3 (Vol%) | Stream 1, C3 | REAL | READ | 7005 | 40020 | N/A | 0 | 100 | VOL% | N/A | N/A
AIT-3108E | Stream_1_iC4 (Vol%) | Stream 1, iC4 | REAL | READ | 7007 | 40022 | N/A | 0 | 100 | VOL% | N/A | N/A
AIT-3108F | Stream_1_nC4 (Vol%) | Stream 1, nC4 | REAL | READ | 7009 | 40024 | N/A | 0 | 100 | VOL% | N/A | N/A
AIT-3108G | Stream_1_C5+ (Vol%) | Stream 1, C5 Plus | REAL | READ | 7011 | 40026 | N/A | 0 | 100 | VOL% | N/A | N/A
| Stream_1_Sample_Mode | Stream 1, Sampling Mode | INT | READ |  | 40028 | N/A | 0 | 3 |  | N/A | N/A | 0=Normal, 1=Get Ready, 2=Ready, 3=Sampling | HMI staus register
| Stream_1_Sample_Mode_HMI_Select | Stream 1, Sampling Mode HMI Select | INT | READ |  | 40029 | N/A | 0 | 2 |  | N/A | N/A | 1 = HMI P2, 2 = HMI P3
| Stream_1_Pressure_Range_Lo | Stream 1, Cell Pressure Scale Low SP | REAL | READ |  | 40030 | N/A | 0 | 10000 | kpa | N/A | N/A
| Stream_1_Pressure_Range_Hi | Stream 1, Cell Pressure Scale High SP | REAL | READ |  | 40032 | N/A | 0 | 10000 | kpa | N/A | N/A
| Stream_1_Pressure_Alarm_Hi_SP | Stream 1, Cell Pressure Scale High Alarm SP | REAL | READ |  | 40034 | N/A | 0 | 10000 | kpa | N/A | N/A
| Stream_1_Temperature_Range_Lo | Stream 1, Cell Temperature Scale Low SP | REAL | READ |  | 40036 | N/A | 0 | 300 | C | N/A | N/A
| Stream_1_Temperature_Range_Hi | Stream 1, Cell Temperature Scale High SP | REAL | READ |  | 40038 | N/A | 0 | 300 | C | N/A | N/A
| Stream_1_Temperature_Alarm_Hi_SP | Stream 1, Cell Temperature Scale High Alarm SP | REAL | READ |  | 40040 | N/A | 0 | 300 | C | N/A | N/A
| Stream_1_BarCodeSeg_1 | Stream 1, BarCode Segment 1 | INT | READ | 7031 | 40042 | N/A | 0 | 100 | MOL% | N/A | N/A
| Stream_1_BarCodeSeg_2 | Stream 1, BarCode Segment 2 | INT | READ | 7033 | 40043 | N/A | 0 | 100 | MOL% | N/A | N/A
| Stream_1_BarCodeSeg_3 | Stream 1, BarCode Segment 3 | INT | READ | 7035 | 40044 | N/A | 0 | 100 | MOL% | N/A | N/A
| spareInt | Spare Holding Register | INT | READ | 7037 | 40045 | N/A | 0 | 100 | MOL% | N/A | N/A
| spareFP | Spare Floating Point Register | REAL | READ | 7039 | 40046 | N/A | 0 | 100 | MOL% | N/A | N/A
| spareFP | Spare Floating Point Register | REAL | READ | 7041 | 40048 | N/A | 0 | 100 | MOL% | N/A | N/A
| spareFP | Spare Floating Point Register | REAL | READ | 7043 | 40050 | N/A | 0 | 100 | MOL% | N/A | N/A
| spareFP | Spare Floating Point Register | REAL | READ | 7045 | 40052 | N/A | 0 | 100 | kPag | N/A | N/A
| spareFP | Spare Floating Point Register | REAL | READ | 7047 | 40054 | N/A | 0 | 150 | kPag | N/A | N/A
AIT-3108Y | spareFP | Spare Floating Point Register | REAL | READ | 7053 | 40056 | N/A | 0 | 100 | % | N/A | N/A
| spareFP | Spare Floating Point Register | REAL | READ |  | 40058 | N/A | 0 | 3 |  | N/A | N/A
| spareFP | Spare Floating Point Register | REAL | R/W |  | 40060 | N/A | 0 | 2 |  | N/A | N/A
AIT-3108Y | Stream_1_Stream_1_Transmission | Stream 1, Transmission | REAL | READ | 7053 | 40062 | N/A | 0 | 100 | % | N/A | N/A | Analyzer Diagnostic Signal
Stream - 2
PIT-4104 | Stream_2_Pressure | Stream 2, Pressure | REAL | READ | 7149 | 40110 | N/A | 0 | 3500 | kPag | N/A | N/A
TIT-4107 | Stream_2_Temperature | Stream 2, Temperature | REAL | READ | 7151 | 40112 | N/A | -20 | 80 | C | N/A | N/A
AIT-4107A | Stream_2_C2_C3_Ratio | Stream 2, C2/C3 Ratio | REAL | READ | 7117 | 40114 | N/A | 0 | 100 | % | N/A | N/A | Calculated as C2 / C3 x 100
AIT-4107B | Stream_2_C1 (Mol%) | Stream 2, C1 | REAL | READ | 7101 | 40116 | N/A | 0 | 100 | VOL% | N/A | N/A
AIT-4107C | Stream_2_C2 (Mol%) | Stream 2, C2 | REAL | READ | 7103 | 40118 | N/A | 0 | 100 | VOL% | N/A | N/A
AIT-4107D | Stream_2_C3 (Mol%) | Stream 2, C3 | REAL | READ | 7105 | 40120 | N/A | 0 | 100 | VOL% | N/A | N/A
AIT-4107E | Stream_2_iC4 (Mol%) | Stream 2, iC4 | REAL | READ | 7107 | 40122 | N/A | 0 | 100 | VOL% | N/A | N/A
AIT-4107F | Stream_2_nC4 (Mol%) | Stream 2, nC4 | REAL | READ | 7109 | 40124 | N/A | 0 | 100 | VOL% | N/A | N/A
AIT-4107G | Stream_2_iC5 (Mol%) | Stream 2, iC5 | REAL | READ | 7111 | 40126 | N/A | 0 | 100 | VOL% | N/A | N/A
AIT-4107H | Stream_2_nC5 (Mol%) | Stream 2, nC5 | REAL | READ | 7113 | 40128 | N/A | 0 | 100 | VOL% | N/A | N/A
AIT-4107I | Stream_2_C6+ (Mol%) | Stream 2, C6 plus | REAL | READ | 7115 | 40130 | N/A | 0 | 100 | VOL% | N/A | N/A
AIT-4107Q | Stream_2_C1_C3_Ratio | Stream 2, C1/C3 Ratio | REAL | READ | 7133 | 40132 | N/A | 0 | 100 | MOL% | N/A | N/A | Calculated as C1 / C3 x 100
AIT-4107Q | Stream_2_Transmission | Stream 2, Transmission | REAL | READ | 7133 | 40136 | N/A | 0 | 100 | MOL% | N/A | N/A
| Stream_2_Sample_Mode | Stream 2, Sampling Mode | INT | READ | 7135 | 40138 | N/A | 0 | 100 | MOL% | N/A | N/A | 0=Normal, 1=Get Ready, 2=Ready, 3=Sampling | HMI staus register
| Stream_2_Sample_Mode_HMI_Select | Stream 2, Sampling Mode HMI Select | INT | READ | 7137 | 40139 | N/A | 0 | 100 | MOL% | N/A | N/A | 1 = HMI P2, 2 = HMI P3
| Stream_2_Pressure_Range_Lo | Stream 2, Cell Pressure Scale Low SP | REAL | READ | 7139 | 40140 | N/A | 0 | 100 | MOL% | N/A | N/A
| Stream_2_Pressure_Range_Hi | Stream 2, Cell Pressure Scale High SP | REAL | READ | 7141 | 40142 | N/A | 0 | 100 | MOL% | N/A | N/A
| Stream_2_Pressure_Alarm_Hi_SP | Stream 2, Cell Pressure Scale High Alarm SP | REAL | READ | 7143 | 40144 | N/A | 0 | 100 | MOL% | N/A | N/A
| Stream_2_Temperature_Range_Lo | Stream 2, Cell Temperature Scale Low SP | REAL | READ | 7145 | 40146 | N/A | 0 | 100 | kPag | N/A | N/A
| Stream_2_Temperature_Range_Hi | Stream 2, Cell Temperature Scale High SP | REAL | READ | 7147 | 40148 | N/A | 0 | 150 | kPag | N/A | N/A
| Stream_2_Temperature_Alarm_Hi_SP | Stream 2, Cell Temperature Scale High Alarm SP | REAL | READ | 7153 | 40150 | N/A | 0 | 100 | % | N/A | N/A
| Stream_2_BarCodeSeg_1 | Stream 2, BarCode Segment 1 | INT | READ | 7031 | 40052 | N/A | 0 | 100 | MOL% | N/A | N/A
| Stream_2_BarCodeSeg_2 | Stream 2, BarCode Segment 2 | INT | READ | 7033 | 40053 | N/A | 0 | 100 | MOL% | N/A | N/A
| Stream_2_BarCodeSeg_3 | Stream 2, BarCode Segment 3 | INT | READ | 7035 | 40054 | N/A | 0 | 100 | MOL% | N/A | N/A
Blue fill denotes tags that are shared on client map