## Stabilizer Bottoms 4107 (CH1)
Stabilized Condensate (CH1)
Species | Reg Type | Reg # | 24_Hr_Avg Reg# | Data Type | Range/Logic
C1 | Input | 7001 | 8001 | 32-bit Floating Point | LV%
C2 | Input | 7003 | 8003 | 32-bit Floating Point | LV%
C3 | Input | 7005 | 8005 | 32-bit Floating Point | LV%
iC4 | Input | 7007 | 8007 | 32-bit Floating Point | LV%
nC4 | Input | 7009 | 8009 | 32-bit Floating Point | LV%
Deemed C4 | Input | 7011 | 8011 | 32-bit Floating Point | LV%
C1_MOL | Input | 7013 | 8013 | 32-bit Floating Point | MOL%
C2_MOL | Input | 7015 | 8015 | 32-bit Floating Point | MOL%
C3_MOL | Input | 7017 | 8017 | 32-bit Floating Point | MOL%
iC4_MOL | Input | 7019 | 8019 | 32-bit Floating Point | MOL%
nC4_MOL | Input | 7021 | 8021 | 32-bit Floating Point | MOL%
iC5_MOL | Input | 7023 | 8023 | 32-bit Floating Point | MOL%
nC5_MOL | Input | 7025 | 8025 | 32-bit Floating Point | MOL%
C6_MOL | Input | 7027 | 8027 | 32-bit Floating Point | MOL%
C7_MOL | Input | 7029 | 8029 | 32-bit Floating Point | MOL%
C8_MOL | Input | 7031 | 8031 | 32-bit Floating Point | MOL%
C9_MOL | Input | 7033 | 8033 | 32-bit Floating Point | MOL%
C10_MOL | Input | 7035 | 8035 | 32-bit Floating Point | MOL%
C11_MOL | Input | 7037 | 8037 | 32-bit Floating Point | MOL%
C12+_MOL | Input | 7039 | 8039 | 32-bit Floating Point | MOL%
Temperature_1 | Input | 7041 | N/A | 32-bit Floating Point | N/A
Pressure_1 | Input | 7043 | N/A | 32-bit Floating Point | N/A
Transmission_1 | Input | 7045 | N/A | 32-bit Floating Point | N/A
Fault_Ireg | Input | 7047 | N/A | 16-bit Integer | N/A
Warning_Ireg | Input | 7048 | N/A | 16-bit Integer | N/A
Alarm IReg | Input | 7049 | N/A | 16-bit Integer | 0=Normal, 1=Warning, 2=Fault
Model IReg | Input | 7050 | N/A | 16-bit Integer | 0=Normal, 1=Warning, 2=Fault
VCON IReg | Input | 7051 | N/A | 16-bit Integer | 41=VCON_Ready
Sample Plan IReg | Input | 7052 | N/A | 16-bit Integer | 41=Trigger to pull sample
Temperature_1 | Holding | 1 | N/A | 16-bit Integer
Pressure_1 | Holding | 2 | N/A | 16-bit Integer
vcon trigger | Holding | 3 | N/A | 16-bit Integer | not used on this app
no flow | Holding | 4 | N/A | 16-bit Integer | 0 = no flow. 1 = flow
vcon_get_ready | Holding | 21 | N/A | 16-bit Integer
vcon_sample | Holding | 22 | N/A | 16-bit Integer
CONFIG SETTINGS
spec_power | Input | 7095 | N/A | 16-bit Integer
Status_Modbus | Input | 7097 | N/A | 16-bit Integer
Beat_Modbus | Input | 7098 | N/A | 16-bit Integer

## De-ethanizer Bottoms 3108 (CH2)
De-Ethanizer Bottoms (CH2)
Species | Reg Type | Reg # | 24_Hr_Avg Reg# | Data Type | Range/Logic
C1 | Input | 7101 | 8101 | 32-bit Floating Point | MOL%
C2 | Input | 7103 | 8103 | 32-bit Floating Point | MOL%
C3 | Input | 7105 | 8105 | 32-bit Floating Point | MOL%
iC4 | Input | 7107 | 8107 | 32-bit Floating Point | MOL%
nC4 | Input | 7109 | 8109 | 32-bit Floating Point | MOL%
iC5 | Input | 7111 | 8111 | 32-bit Floating Point | MOL%
nC5 | Input | 7113 | 8113 | 32-bit Floating Point | MOL%
C6+ | Input | 7115 | 8115 | 32-bit Floating Point | MOL%
C1/C3 Ratio | Input | 7117 | 8117 | 32-bit Floating Point | unitless
C2/C3 Ratio | Input | 7119 | 8119 | 32-bit Floating Point | unitless
Temperature_2 | Input | 7121 | N/A | 32-bit Floating Point | N/A
Pressure_2 | Input | 7123 | N/A | 32-bit Floating Point | N/A
Transmission_2 | Input | 7125 | N/A | 32-bit Floating Point | N/A
Fault_Ireg | Input | 7127 | N/A | 16-bit Integer | N/A
Warning_Ireg | Input | 7128 | N/A | 16-bit Integer | N/A
Alarm IReg | Input | 7130 | N/A | 16-bit Integer | 0=Normal, 1=Warning, 2=Fault
Model IReg | Input | 7131 | N/A | 16-bit Integer | 0=Normal, 1=Warning, 2=Fault
VCON IReg | Input | 7132 | N/A | 16-bit Integer | 41=VCON_Ready
Sample Plan IReg | Input | 7133 | N/A | 16-bit Integer | 41=Trigger to pull sample