## CLIENT MODBUS MAP
| OVINTIV - PIPESTONE PPF MODBUS MAP | [12 empty] | VERIFIED 2024-08-12
| Tag Number | PLC Tag | Service Description (Max=32 Characters) | Data Type | Read/Write | OBC ModBus Address | PLC ModBus Address | Bit | Min Range | Max Range | Eng Unit | STATUS 0 | STATUS 1 | Comments | ADDITIONAL COMMENTS
1 | RESET | RESET | Reset Alarm | BOOL | WRITE |  | 00001 | N/A | N/A | N/A | N/A | OFF | RESET | Pulse for 2 seconds to reset latched alarms
2 | OBC_COMM_FAIL | OBC_COMM_FAIL | On Board Computer Communication Fault | BOOL | READ |  | 00002 | N/A | N/A | N/A | N/A | FAULT | OK | Indicates failure between On Board Computer and PLC
3 | STREAM - 1
4 | UA_3108A | Stream_1_Analyzer_Warning | Stream 1-Analyzer Common Warning Alarm | BOOL | READ |  | 00010 | N/A | N/A | N/A | N/A | OFF | WARNING | Non Latching
5 |  | Stream_1_Model_Warning | Stream 1 - Model Quality Warning | BOOL | READ |  | 00011 | N/A | N/A | N/A | N/A | OFF | WARNING | Non Latching
6 | UA_3108B | Stream_1_Sample_Panel_Warning | Stream 1-Sample Panel Common Warning Alarm | BOOL | READ |  | 00012 | N/A | N/A | N/A | N/A | OFF | WARNING | Warning Local To Sample System Enclosure
7 | FSL_3108 | Stream_1_FSL_COND | Stream 1 - Low Sample Flow Warning | REAL | READ |  | 00013 | N/A | N/A | N/A | N/A | OFF | WARNING | Non Latching, 2 min delay for interrupt valve control
8 | FSH_3108 | Stream_1_FSH_COND | Stream 1 - High Sample Flow Warning | REAL | READ |  | 00014 | N/A | N/A | N/A | N/A | OFF | WARNING | Not Required
9 | PAH-3108 | Stream_1_High_Pressure_Alarm | Stream 1 - High Pressure Warning Alarm | BOOL | READ |  | 00015 | N/A | N/A | N/A | N/A | OFF | WARNING | Latching, 1 sec debounce
10 | TAH-3108 | Stream_1_High_Temperature_Alarm | Stream 1 - High Temperature Warning Alarm | BOOL | READ |  | 00016 | N/A | N/A | N/A | N/A | OFF | WARNING | Latching, 1 sec debounce
11 |  | Stream_1_Sampling_Alarm | Stream 1 - Sample Switch Warning | BOOL | READ |  | 00017 | N/A | N/A | N/A | N/A | OFF | WARNING | Left in SAMPLE mode > 20 min
12 | XA_3108A | Stream_1_Analyzer_Fault | Stream 1-Analyzer Common Fault Alarm | BOOL | READ |  | 00018 | N/A | N/A | N/A | N/A | OFF | FAULT | Non Latching
13 |  | Stream_1_Model_Fault | Stream 1 - Model Quality Fault | BOOL | READ |  | 00019 | N/A | N/A | N/A | N/A | OFF | FAULT | Non Latching
14 | XA_3108B | Stream_1_Sample_Panel_Fault | Stream 1-Sample Panel Common Fault Alarm | BOOL | READ |  | 00020 | N/A | N/A | N/A | N/A | OFF | FAULT | Faut Local To Sample System Enclosure
15 |  | Stream_1_Spare | Stream 1 - Spare | BOOL | READ |  | 00021 | N/A | N/A | N/A | N/A | OFF | FAULT | Not Used
16 |  | Stream_1_Temperature_Fault | Stream 1 - Temperature Transmitter Fault | BOOL | READ |  | 00022 | N/A | N/A | N/A | N/A | OFF | FAULT | Latching
17 |  | Stream_1_Pressure_Fault | Stream 1 - Pressure Transmitter Fault | BOOL | READ |  | 00023 | N/A | N/A | N/A | N/A | OFF | FAULT | Latching
18 |  | Stream_1_VCON_Normal | Stream 1 - Analyzer In Continous Analysis Mode | BOOL | READ |  | 00024 | N/A | N/A | N/A | N/A | FALSE | TRUE | Sample Collection Control
19 |  | Stream_1_VCON_Get_Ready | Stream 1 - Analyzer Sample Collection Mode Request | BOOL | READ |  | 00025 | N/A | N/A | N/A | N/A | FALSE | TRUE | Sample Collection Control
20 |  | Stream_1_VCON_Sampling | Stream 1 - Analyzer in Sample Collection Mode | BOOL | READ |  | 00026 | N/A | N/A | N/A | N/A | FALSE | TRUE | Sample Collection Control
21 |  | Stream_1_VCON_Ready | Stream 1 - Analyzer Ready For Sample Collection | BOOL | READ |  | 00027 | N/A | N/A | N/A | N/A | FALSE | TRUE | Sample Collection Control
22 |  | Stream_1_Sample_Source | Stream 1 - Sample Request Source | BOOL | READ |  | 00028 | N/A | N/A | N/A | N/A | HMI | SWITCH | Sample Control HMI or Handswitch | Always true for this application
23 |  | Stream_1_Active_Alarm | Stream 1 - Active Alarm | BOOL | READ |  | 00029 | N/A | N/A | N/A | N/A | OFF | ALARM | Status bit for HMI graphics
24 | STREAM - 2
25 | UA_4107A | Stream_2_Analyzer_Warning | Stream 2-Analyzer Common Warning Alarm | BOOL | READ |  | 00050 | N/A | N/A | N/A | N/A | OFF | WARNING | Warning Local To Analyzer Control Cabinet
26 |  | Stream_2_Model_Warning | Stream 2 - Analyzer Model Quality Warning | BOOL | READ |  | 00051 | N/A | N/A | N/A | N/A | OFF | WARNING | Calibration Quality
27 | UA-4107B | Stream_2_Sample_Panel_Warning | Stream 2-Sample Panel Common Warning Alarm | BOOL | READ |  | 00052 | N/A | N/A | N/A | N/A | OFF | WARNING | Warning Local To Sample System Enclosure
28 | FSL_4107 | Stream_2_FSL_COND | Stream 2 - Low Sample Flow Warning | REAL | READ |  | 00053 | N/A | N/A | N/A | N/A | OFF | WARNING | No Flow Condition at Sample Cell
29 | FSH-4107 | Stream_2_FSH_COND | Stream 2 - High Sample Flow Warning | REAL | READ |  | 00054 | N/A | N/A | N/A | N/A | OFF | WARNING | Hi Flow Condition at Sample Cell
30 | PAH-4107 | Stream_2_High_Pressure_Alarm | Stream 2 - High Pressure Warning Alarm | BOOL | READ |  | 00055 | N/A | N/A | N/A | N/A | OFF | WARNING | Setpoint Local to HMI
31 | TAH-4107 | Stream_2_High_Temperature_Alarm | Stream 2 - High Temperature Warning Alarm | BOOL | READ |  | 00056 | N/A | N/A | N/A | N/A | OFF | WARNING | Setpoint Local to HMI
32 |  | Stream_2_Sampling_Alarm | Stream 2 - Sample Switch Warning | BOOL | READ |  | 00057 | N/A | N/A | N/A | N/A | OFF | WARNING | Left in SAMPLE mode > 20 min
33 | XA-4107A | Stream_2_Analyzer_Fault | Stream 2-Analyzer Common Fault Alarm | BOOL | READ |  | 00058 | N/A | N/A | N/A | N/A | OFF | FAULT | Faut Local To Analyzer Control Cabinet
34 |  | Stream_2_Model_Fault | Stream 2 - Analyzer Model Quality Fault | BOOL | READ |  | 00059 | N/A | N/A | N/A | N/A | OFF | FAULT | Calibration Quality
35 | XA-4107B | Stream_2_Sample_Panel_Fault | Stream 2-Sample Panel Common Fault Alarm | BOOL | READ |  | 00060 | N/A | N/A | N/A | N/A | OFF | FAULT | Faut Local To Sample System Enclosure
36 |  | Stream_2_Spare | Stream 2 - Spare | BOOL | READ |  | 00061 | N/A | N/A | N/A | N/A | OFF | FAULT | Hardware Fault | Not Used
37 |  | Stream_2_Temperature_Fault | Stream 2 - Temperature Transmitter Fault | BOOL | READ |  | 00062 | N/A | N/A | N/A | N/A | OFF | FAULT | Hardware Fault
38 |  | Stream_2_Pressure_Fault | Stream 2 - Pressure Transmitter Fault | BOOL | READ |  | 00063 | N/A | N/A | N/A | N/A | OFF | FAULT | Hardware Fault
39 |  | Stream_2_VCON_Normal | Stream 2 - Analyzer In Continous Analysis Mode | BOOL | READ |  | 00064 | N/A | N/A | N/A | N/A | FALSE | TRUE | Sample Collection Control
40 |  | Stream_2_VCON_Get_Ready | Stream 2 - Analyzer Sample Collection Mode Request | BOOL | READ |  | 00065 | N/A | N/A | N/A | N/A | FALSE | TRUE | Sample Collection Control
41 |  | Stream_2_VCON_Sampling | Stream 2 - Analyzer in Sample Collection Mode | BOOL | READ |  | 00066 | N/A | N/A | N/A | N/A | FALSE | TRUE | Sample Collection Control
42 |  | Stream_2_VCON_Ready | Stream 2 - Analyzer Ready For Sample Collection | BOOL | READ |  | 00067 | N/A | N/A | N/A | N/A | FALSE | TRUE | Sample Collection Control
43 |  | Stream_2_Sample_Source | Stream 2 - Sample Request Source | BOOL | READ |  | 00068 | N/A | N/A | N/A | N/A | HMI | SWITCH | Sample Control HMI or Handswitch | Always true for this application
44 |  | Stream_2_Active_Alarm | Stream 2 - Active Alarm | BOOL | READ |  | 00069 | N/A | N/A | N/A | N/A | OFF | ALARM | Status bit for HMI graphics
45 | Holding Registers
46 | CT_3112 | CT_3112 | Communications Heartbeat Register to DCS | INT | READ |  | 40001 | N/A | 0 | 60 | N/A | N/A | N/A | PLC Clock Seconds passed onto master controller. Alarm if value has not changed after set time. | A communications failure will interupt both channels.
47 | PLC_YEAR | PLC_YEAR | PLC Clock Year | INT | READ |  | 40002 |  | 2016 | 2116 |  |  |  | Real Time Clock From PLC
48 | PLC_MONTH | PLC_MONTH | PLC Clock Month | INT | READ |  | 40003 |  | 1 | 12 |  |  |  | Real Time Clock From PLC
49 | PLC_DAY | PLC_DAY | PLC Clock Day | INT | READ |  | 40004 |  | 1 | 31 |  |  |  | Real Time Clock From PLC
50 | PLC_HOUR | PLC_HOUR | PLC Clock Hour | INT | READ |  | 40005 |  | 0 | 24 |  |  |  | Real Time Clock From PLC
51 | PLC_MINUTE | PLC_MINUTE | PLC Clock Minute | INT | READ |  | 40006 |  | 0 | 60 |  |  |  | Real Time Clock From PLC
52 | PLC_SECOND | PLC_SECOND | PLC Clock Second | INT | READ |  | 40007 |  | 0 | 60 |  |  |  | Real Time Clock From PLC
53 | STREAM - 1
54 | PIT-3108 | Stream_1_Pressure_1 | Stream 1, Pressure | REAL | READ | 7049 | 40010 | N/A | 0 | 3500 | kPag | N/A | N/A
55 | TIT-3108 | Stream_1_Temperature_1 | Stream 1, Temperature | REAL | READ | 7051 | 40012 | N/A | -20 | 80 | C | N/A | N/A
56 | AIT-3108A | Stream_1_Deemed C4 | Stream 1, Deemed C4- calculated as: Deemed C4- = (3*(%C1+%C2+%C3)) + (%iC4+%nC4) | REAL | READ | 7017 | 40014 | N/A | 0 | 100 | % | N/A | N/A
57 | AIT-3108B | Stream_1_C1 (Vol%) | Stream 1, C1 | REAL | READ | 7001 | 40016 | N/A | 0 | 100 | VOL% | N/A | N/A
58 | AIT-3108C | Stream_1_C2 (Vol%) | Stream 1, C2 | REAL | READ | 7003 | 40018 | N/A | 0 | 100 | VOL% | N/A | N/A
59 | AIT-3108D | Stream_1_C3 (Vol%) | Stream 1, C3 | REAL | READ | 7005 | 40020 | N/A | 0 | 100 | VOL% | N/A | N/A
60 | AIT-3108E | Stream_1_iC4 (Vol%) | Stream 1, iC4 | REAL | READ | 7007 | 40022 | N/A | 0 | 100 | VOL% | N/A | N/A
61 | AIT-3108F | Stream_1_nC4 (Vol%) | Stream 1, nC4 | REAL | READ | 7009 | 40024 | N/A | 0 | 100 | VOL% | N/A | N/A
62 | AIT-3108G | Stream_1_C5+ (Vol%) | Stream 1, C5 Plus | REAL | READ | 7011 | 40026 | N/A | 0 | 100 | VOL% | N/A | N/A
63 |  |  |  | REAL | READ | 7013 | 40028 | N/A | 0 | 100 | VOL% | N/A | N/A | Unused Register.
64 |  |  |  | REAL | READ | 7015 | 40030 | N/A | 0 | 100 | VOL% | N/A | N/A | Unused Register.
65 | AIT-3108J | Stream_1_C1 (Mol%) | Stream 1, C1 | REAL | READ | 7019 | 40032 | N/A | 0 | 100 | MOL% | N/A | N/A | Component Removed
66 | AIT-3108K | Stream_1_C2 (Mol%) | Stream 1, C2 | REAL | READ | 7021 | 40034 | N/A | 0 | 100 | MOL% | N/A | N/A | Component Removed
67 | AIT-3108L | Stream_1_C3 (Mol%) | Stream 1, C3 | REAL | READ | 7023 | 40036 | N/A | 0 | 100 | MOL% | N/A | N/A | Component Removed
68 | AIT-3108M | Stream_1_iC4 (Mol%) | Stream 1, iC4 | REAL | READ | 7025 | 40038 | N/A | 0 | 100 | MOL% | N/A | N/A | Component Removed
69 | AIT-3108N | Stream_1_nC4 (Mol%) | Stream 1, nC4 | REAL | READ | 7027 | 40040 | N/A | 0 | 100 | MOL% | N/A | N/A | Component Removed
70 | AIT-3108O | Stream_1_iC5 (Mol%) | Stream 1, iC5 | REAL | READ | 7029 | 40042 | N/A | 0 | 100 | MOL% | N/A | N/A | Component Removed
71 | AIT-3108P | Stream_1_nC5 (Mol%) | Stream 1, nC5 | REAL | READ | 7031 | 40044 | N/A | 0 | 100 | MOL% | N/A | N/A | Component Removed
72 | AIT-3108Q | Stream_1_C6 (Mol%) | Stream 1, C6 | REAL | READ | 7033 | 40046 | N/A | 0 | 100 | MOL% | N/A | N/A | Component Removed
73 | AIT-3108R | Stream_1_C7 (Mol%) | Stream 1, C7 | REAL | READ | 7035 | 40048 | N/A | 0 | 100 | MOL% | N/A | N/A | Component Removed
74 | AIT-3108S | Stream_1_C8 (Mol%) | Stream 1, C8 | REAL | READ | 7037 | 40050 | N/A | 0 | 100 | MOL% | N/A | N/A | Component Removed
75 | AIT-3108T | Stream_1_C9 (Mol%) | Stream 1, C9 | REAL | READ | 7039 | 40052 | N/A | 0 | 100 | MOL% | N/A | N/A | Component Removed
76 | AIT-3108U | Stream_1_C10 (Mol%) | Stream 1, C10 | REAL | READ | 7041 | 40054 | N/A | 0 | 100 | MOL% | N/A | N/A | Component Removed
77 | AIT-3108V | Stream_1_C11 (Mol%) | Stream 1, C11 | REAL | READ | 7043 | 40056 | N/A | 0 | 100 | MOL% | N/A | N/A | Component Removed
78 | AIT-3108W | Stream_1_C12 (Mol%) | Stream 1, C12 | REAL | READ | 7045 | 40058 | N/A | 0 | 100 | kPag | N/A | N/A | Component Removed
79 |  | Stream_1_Vapour_Press | Stream 1, Vapour Pressure | REAL | READ | 7047 | 40060 | N/A | 0 | 150 | kPag | N/A | N/A | Component Removed
80 | AIT-3108Y | Stream_1_Stream_1_Transmission | Stream 1, Transmission | REAL | READ | 7053 | 40062 | N/A | 0 | 100 | % | N/A | N/A | Analyzer Diagnostic Signal
89 | Stream - 2
90 | PIT-4104 | Stream_2_Pressure | Stream 2, Pressure | REAL | READ | 7149 | 40110 | N/A | 0 | 3500 | kPag | N/A | N/A
91 | TIT-4107 | Stream_2_Temperature | Stream 2, Temperature | REAL | READ | 7151 | 40112 | N/A | -20 | 80 | C | N/A | N/A
92 | AIT-4107A | Stream_2_C2_C3_Ratio | Stream 2, C2/C3 Ratio | REAL | READ | 7117 | 40114 | N/A | 0 | 100 | % | N/A | N/A | Calculated as C2 / C3 x 100
93 | AIT-4107B | Stream_2_C1 (Mol%) | Stream 2, C1 | REAL | READ | 7101 | 40116 | N/A | 0 | 100 | VOL% | N/A | N/A
94 | AIT-4107C | Stream_2_C2 (Mol%) | Stream 2, C2 | REAL | READ | 7103 | 40118 | N/A | 0 | 100 | VOL% | N/A | N/A
95 | AIT-4107D | Stream_2_C3 (Mol%) | Stream 2, C3 | REAL | READ | 7105 | 40120 | N/A | 0 | 100 | VOL% | N/A | N/A
96 | AIT-4107E | Stream_2_iC4 (Mol%) | Stream 2, iC4 | REAL | READ | 7107 | 40122 | N/A | 0 | 100 | VOL% | N/A | N/A
97 | AIT-4107F | Stream_2_nC4 (Mol%) | Stream 2, nC4 | REAL | READ | 7109 | 40124 | N/A | 0 | 100 | VOL% | N/A | N/A
98 | AIT-4107G | Stream_2_iC5 (Mol%) | Stream 2, iC5 | REAL | READ | 7111 | 40126 | N/A | 0 | 100 | VOL% | N/A | N/A
99 | AIT-4107H | Stream_2_nC5 (Mol%) | Stream 2, nC5 | REAL | READ | 7113 | 40128 | N/A | 0 | 100 | VOL% | N/A | N/A
100 | AIT-4107I | Stream_2_C6+ (Mol%) | Stream 2, C6 plus | REAL | READ | 7115 | 40130 | N/A | 0 | 100 | VOL% | N/A | N/A
108 | AIT-4107Q | Stream_2_C1_C3_Ratio | Stream 2, C1/C3 Ratio | REAL | READ | 7133 | 40132 | N/A | 0 | 100 | MOL% | N/A | N/A | Calculated as C1 / C3 x 100
108 | AIT-4107Q | Stream_2_Transmission | Stream 2, Transmission | REAL | READ | 7133 | 40136 | N/A | 0 | 100 | MOL% | N/A | N/A
Blue fill denotes tags that are shared on client map

## DataTypes (hidden)
Data Type | Description
BOOL | Boolean, Single bit
WORD | Unsigned 16 bit value bit 0 is the low bit bit 15 is the high bit
SHORT | Signed 16 bit value bit 0 is the low bit bit 14 is the high bit bit 15 is the sign bit
DWORD | Unsigned 32 bit value bit 0 is the low bit bit 31 is the high bit
LONG | Signed 32 bit value bit 0 is the low bit bit 30 is the high bit bit 31 is the sign bit
BCD | Two byte packed BCD Value range is 0-9999. Behavior is undefined for values beyond this range.
LBCD | Four byte packed BCD Value range is 0-99999999. Behavior is undefined for values beyond this range.
STRING | Null terminated ASCII string Supported on Modbus Model, includes Hi-Lo Lo-Hi byte order selection.
DOUBLE (Note 1) | 64 bit floating point value The driver interprets four consecutive registers as a double precision value by making the last two registers the high DWord and the first two registers the low DWord.
DOUBLE Example | If register 40001 is specified as a double, bit 0 of register 40001 would be bit 0 of the 64 bit data type and bit 15 of register 40004 would be bit 63 of the 64 bit data type.
FLOAT (Note 1) | 32 bit floating point value The driver interprets two consecutive registers as a single precision value by making the last register the high word and the first register the low word.
FLOAT Example | If register 40001 is specified as a float, bit 0 of register 40001 would be bit 0 of the 32 bit data type and bit 15 of register 40002 would be bit 31 of the 32 bit data type.
Notes:
1. The descriptions assume the default; that is, first DWord low data handling of 64 bit data types and first word
low data handling of 32 bit data types.
2. Standard data format names have been selected. If other names are desired, specify the bytes and range.